#### ATTACHMENT – TECHNICAL SPECIFICATION FORM

TENDER No. PROSOFT NO 91189746

Bidders are requested to complete this form, sign it and return it as part of their bid submission. The bidder shall fill in this form in accordance with the instructions indicated. No alterations to its format shall be permitted and no substitutions shall be accepted.

This technical specification form has an integral part with the Bid Price Form for this tender.

Date: [Insert submission date]

Name of the Bidder: [Insert the company name]

Subject       System for Tri-Chamber Solar CS,   Inquiry  91189746    dated 29.08.2025

| No | Requirement Specification | Picture (as sample, not mandatory brand) | Confirmation of Compliance to the Specification | Proposed Brand Type & Specification (please mention the detail specification) | Please attached “Brochure or Catalog” |
| --- | --- | --- | --- | --- | --- |
|  | Note: The Bidder is not allowed to quote more than one item (options) with different price for one kind of item requested. The vendors who do not comply will be ruled out from the tender evaluation Catatan: Peserta tender tidak diijinkan untuk memberikan penawaran lebih dari satu jenis (pilihan) dengan harga yang berbeda untuk setiap item yang diminta. Vendor yang tidak mematuhi hal di atas, tidak akan diikut sertakan dalam evaluasi. Remarks: The specification proposed shall be clear, details (brand, type, details specs) and not ambiguous. This is very important part for the evaluation process. |  |  |  |  |
| A | Solar System EQUIPMENT (COMPONENT) |  |  |  |  |
| 1 | Mounting System 6 units Photovoltaic roof mounting system for 6 strings • Mounting System Type: Rail-based aluminum mounting system, suitable for pitched roofs with metal surfaces. • Security (Anti-theft) screws for fixing the PV panels must be utilized. • The mounting system brackets must be securely attached to the roof to be able to withstand wind loads on the mounting system - The modules and structures need to be able to support wind loads of up to 58 m/s (category 3 storms). |  |  |  |  |
| 2 | Wiring and cables 70 m Solar Flex Copper Cable All necessary cables, plugs and associated materials must be included in the delivery. Insulated, stranded, flexible copper wiring should be used for DC systems. All wiring must be suitable for the intended uses and labelled as such. All cables must be double insulated, ozone, weather and UV resistant, halogen free, resistant to acid and bases. Flame retardant to DIN VDE 0482-332-1-2, DIN EN 60332-1-2. Hydrolysis and ammoniac resistant. Rodent protection and VDE, TüV, UL approved. The cross section and maximum length should follow the indications of the wiring diagrams. Cables used for the electrical connection between loads and batteries must be flexible, high conductivity copper conductors, insulated and colour coded with a general purpose PVC jacket. Connections to the battery must be made using the correct size terminals, depending on the type of battery. Field installed wiring should be terminated using terminal blocks or screw connectors. All connections must be made in watertight junction boxes. Single wires should be installed in neat, good quality conduits. Insulating materials must comply with the heat and fire resistance requirements stipulated by international standards (UTE or IEE). DC connections must have clearly labelled polarity. Cable canals need to be used for all wiring between components. Following minimum requirements must be fulfilled: Temperature Range: -40 to 90 °C Maximum Temperature at Conductor: 120 °C Short Circuit Temperature: 200 °C for up to 5 seconds Nominal Voltage (VDE): 600 / 1000 VAC / 1800 V DC conductor to conductor AC Test Voltage: 10,000 V Highest Permissible Voltage: DC: conductor/conductor 1.8 kV, conductor/earth 0.9 kV AC: conductor/earth 0.9 kV Three-phase: conductor/conductor 1.2 kV |  |  |  |  |
| 3 | PV Combiner Box 3 Units Number of Inputs (Strings): 2 Input Voltage Range: 200 – 1000 V DC Maximum Input Current per String: 15 A 2 × String Fuses ( 15 A ) Surge Protection Device Reverse polarity protection 1 × DC Circuit Breaker or Load Break Switch Material: Powder-coated steel or polycarbonate UV and corrosion resistant Protection Rating:IP66 Pre-installed cable glands or MC4 connectors Operating Temperature: -25 °C to +60 °C Mounting: Wall-mounted |  |  |  |  |
| 4 | Energy Meter 3 Units Energy Meter For monitoring energy consumption. 230 V AC 1 Phase Modbus TCP type. Open register suitable for PCL systems Up to 25 A |  |  |  |  |
| 5 | Battery 6 Units Lithium-Ion Type LiFePO4 48 V DC batteries The batteries need to be compatible with the off-grid inverter as listed on the official green list by the respective inverter manufacturer for compatible batteries. Non-Toxic & Non-Hazardous Cobalt-Free LFP Chemistry with Built-In Safety Battery Management System is mandatory. CAN communication interface, integrated circuit-breaker and IP65 waterproof is mandatory. The number of batteries is specified in Annex 1 for each site. The batteries must be connected in parallel. Positive and negative polarity must be clearly indicated. Each battery must be labelled with at least: Manufacturer, type, model number, voltage rating, capacity, and year of manufacture. Compliance with EN IEC 61000-6-2:2019, IEC 62619:2017, ICE63056:2020 and VDE-AR- 2510-50:2017 is required. Compliance with CE is mandatory. Voltage Range: 44.5 - 59 V DC Rated Capacity: 4.75 - 5.25 kWh Peak Current: 135 - 250 A DC Continuous Charge Current: 80 - 150 A DC Efficiency: 96 - 98% Operation Temperature: 0 - 45 °C Relative Humidity Range: 5 - 95% Number of Cycles: 6,000 at 80% DOD |  |  |  |  |
| 6 | Battery Fuses 5 Units DC Fuse 15Ampere |  |  |  |  |
| 7 | Main Box 1 Units Main switch board box IP 54 |  |  |  |  |
| 8 | Surge Protection Device (SPD) 12 Units Type 1,2 and 3 ((AC and DC based on wiring diagram) |  |  |  |  |
| 9 | Residual Current Device (RCD) 2 Unit Connected to various MCBs based on wiring diagram |  |  |  |  |
| 10 | Battery Fuse 2 Unit 200 Ampere |  |  |  |  |
| 11 | Miniature Circuit Breaker (MCB) 20 Unit 6A, 16A, 20A, 40A; Type C; DP AC output/input based on wiring diagram: IEC 60947-2 Compliance |  |  |  |  |
| 12 | Busbar 2 Unit L busbar, N busbar; 25mm x 3mm |  |  |  |  |
| 13 | Isolator Switch 4 Unit For various AC input/output paths 230 V AC according wiring diagram |  |  |  |  |
| 14 | AC/DC Converter 1 Unit Input 230V AC Output 24 VDC |  |  |  |  |
| 15 | AC Cables and installation materials 1 Unit Conduits, trays, ducts, clips, ties, glands, and junction boxes According to wiring diagram |  |  |  |  |
| 16 | PV Inverter 3 units PV generator power: 7,500 Wp. Maximum input voltage: 600 V. MPP voltage range: 140 V – 500 V. Max. input current per MPPT: 15 A. Number of MPP trackers: 2. Rated AC power: 4,000 kVA Nominal AC voltage: 230 V. AC frequency: 50 Hz. Max. output current: 22 A. Efficiency: 97.0 %. Protection rating: IP65. Communication protocols: Modbus TCP (Preferable SMA Sunny Boy 4.0 due to a current cooperation with one of our partners) |  |  |  |  |
| 17 | Off-Grid Battery Inverter 1 Unit AC Input Power : 11,500 kVA Off-Grid AC Power (at 25 °C): 6,000 kVA (continuous), 8,000 kVA for 30 minutes, 11,000 kVA for 3 seconds AC Voltage (Output): 230 V ± 2% AC Frequency: 50/60 Hz (automatic detection) Battery Voltage Range: 41 V to 63 V Efficiency: 95.8% Protection Class: IP54 Cooling: Temperature-controlled fan Communication protocols: Modbus TCP (Preferable SMA Sunny Island 8.0 due to a current cooperation with one of our partners) |  |  |  |  |
| 18 | Inverter Energy Meter 2 units For assuring net-zero energy balance at grid point (conected and compatible to the selected PV inverters) - Connection to the local router via Ethernet cable (10/100 Mbit/s, RJ45 plug) - Inputs (voltage and current): Nominal voltage 230 V/400 V Frequency 50 Hz/±5% Nominal current / limiting current per line conductor 5 A/63 A (>63 A can be connected via external current transformers) Start-up current < 25 mA - Protection class (according to IEC 62103) II - Degree of protection (according to IEC 60529) IP2X |  |  |  |  |
| 19 | Pyranometer 1 unit Weather station including Irradiance sensor and temperature ISO 9060 spectrally flat Class C 0 to 1 Volt or 4 to 20 mA analogue output No change of desiccant for 10 years Active temperature correction from -40 °C to +80 °C temperature response < 5 % (-10 °C to +40 °C) |  |  |  |  |
| B | MANPOWER (subject to income tax) Consist of: - Expert fee - Travel Expenses (transport, accommodation and daily allowance) - Income tax included |  |  |  |  |
| 20 | Engineering - Project Management (include as build drawing) - Permit and regulation compliance (NIDI, PLN Application, IUPTLS, SLO) |  |  |  |  |
| 2 | Installation - Installation and commissioning, training post installation. |  |  |  |  |
| 3 | Maintenance (1 year) 2 times regular maintenance (at 6 and 12 months after installation) |  |  |  |  |

| TERMS AND CONDITIONS: |  | Please tick “Yes” or ”No” |  | Deviations |
| --- | --- | --- | --- | --- |
| 1 | Product shall be delivered by the contractor after the PO release. Delivery date estimation : 31 October 2025 | ☐ Yes ☐ No |  |  |
| 2 | The contractor shall deliver the goods within 30 days after signing the Purchase order (date) in the delivery address as mentioned above Delivery Address: On Behalf of Project Cooperation with GIZ x IPB Agribusiness and Technology Park (ATP) IPB Jl. Carang Pulang No.1, Cikarawang, Kec. Dramaga, Kabupaten Bogor, Jawa Barat 16680 | ☐ Yes ☐ No |  |  |
| 3 | Validity of Quotation is 100 calendar days |  YES |  NO |  |
| 4 | Payment terms: 2 – 3 months of receipt of the Supplier's invoice and delivery receipt of the goods specified in the Purchase Order, with detailed: - 70% from total Equipment cost upon completed delivery on site - 20% from total Equipment cost and 90% from installation cost upon completed installation - 50% from Maintenance cost upon completed 1st maintenance at 6th month after success installation - Final Payment 10% Equipment and installation cost & 50% Maintenance coat at 12th month after success installation The payment terms and conditions will follow the tax exemption process of the Government of Indonesia. |  YES |  NO |  |
| 5 | All prices/rates quoted must be exclusive of all taxes, since the GIZ, including its subsidiary organs, is exempt from taxes according to the PMK No. 215/PMK 03/2008 and KMK No. 17/KMK 010/Year 2021. GIZ shall process the VAT with tax exemption to BADORA. The process of tax exemption will take 2 - 3 months. Supplier is obliged to release the Tax Invoice with code 08 (tax exemption). Please provide the PKP and/ PTKP Letter. |  YES |  NO |  |
| 6 | Supplier Self-Declaration to determine the origin or source of the goods offered shall be signed and attached with the tender document (obligatory) – as annex 3 |  YES |  NO |  |
| 7 | Declaration of Prevention of Terrorism shall be signed and attached with the tender document – as annex 4 |  YES |  NO |  |
| 8 | Original items with official warranty |  YES |  NO |  |
| 9 | Supplier shall demonstrate verifiable experience in the design, supply, installation, and commissioning of off-grid solar PV systems, preferably with battery storage and inverter integration with SMA systems to ensure overall compatibility as per required design. |  YES |  NO |  |
| 10 | Supplier have successfully completed projects of similar size (≥10 kW solar PV, battery system, hybrid inverters) within the past five (5) years. |  YES |  NO |  |
| 11 | Supplier already secures a quota for installation within 2025 because the project includes a solar PV rooftop system connected to the PLN grid. |  YES |  NO |  |
| 12 | Supplier must provide references and photos from past projects. |  YES |  NO |  |
| 13 | Supplier must provide SBUJPTL (Sertifikat Badan Usaha Jasa Penunjang Tenaga Listrik), issued by Lembaga Sertifikasi Badan Usaha (LSBU) that has been accredited or appointed by the Minister of Energy and Mineral Resources. |  YES |  NO |  |
| 14 | Installation personnel must provide SKKTK (Sertifikat Kompetensi Tenaga Teknik Ketenagalistrikan) issued by The Ministry of Energy and Mineral Resources, where the supervisor has a minimum of Level 5 SKKTK on PV system installation. |  YES |  NO |  |
| 15 | Supplier shall have an established local office or partner in Java, Indonesia to ensure responsive after-sales service, maintenance, and warranty support. |  YES |  NO |  |
| 16 | Supplier must have Health, Safety, and Environmental Compliance, (e.g.: Use of appropriate personal protective equipment (PPE) during installation.) and all personnel covered with BPJS Ketenagakerjaan |  YES |  NO |  |
| 17 | Supplier must comply with national electrical and construction safety standards, manufacturer installation manuals, project-specific technical requirements and commissioning (i.e.: Implementation of best practices to prevent damage to the roof and solar equipment.) |  YES |  NO |  |
| 18 | Supplier shall review all drawings and specifications, notify any discrepancies and submit a detailed drawing to GIZ maximum 3 weeks after signature of the contract. |  YES |  NO |  |
| 19 | Supplier will visit the installation site at IPB Bogor prior to start of installation to organize the installation work and for assessment of potential amendments |  YES |  NO |  |
| 20 | Supplier will coordinate arrangements and timeline with IPB University, Fresh Factory, and GIZ regarding supply and installation works. |  YES |  NO |  |
| 21 | Supplier should be responsible for the packing/pre-assembly. |  YES |  NO |  |
| 22 | Supplier provides a warehouse to store equipment prior to delivery on site |  YES |  NO |  |
| 23 | Supplier will be responsible for goods transport and its cost to the site and installation of the system |  YES |  NO |  |
| 24 | Supplier will install the PV modules (already on site) and mounting structure in the roof, ensuring all modules are installed with appropriate spacing, grounding, and mechanical fixation as per technical guidelines |  YES |  NO |  |
| 25 | After installation, the Supplier shall submit the Fit for Operational certificate (Sertifikat Layak Operasional) issued by LIT (Lembaga Inspeksi Teknik). |  YES |  NO |  |
| 26 | A final test will be carried out to demonstrate that the Systems can be operated according to the technical specifications under all available operating conditions |  YES |  NO |  |
| 27 | Supplier shall submit a quality checklist, along with the completeness of drawings, operation and maintenance manuals, witnessed and approved by GIZ |  YES |  NO |  |
| 28 | Supplier shall complete the supply and transport equipment to site, installation of equipment, including the materials provided by GIZ, and the test and commission of the installation within Q4 of 2025 |  YES |  NO |  |
| 29 | Supplier will provide 2 Maintenance services at 6th month and 12th month after installation and the contractor will be responsible for the cost of replacing any malfunction component upon submitting a maintenance report to GIZ. |  YES |  NO |  |
| 30 | Supplier must provide a minimum of two (2) years warranty on the entire system and components (only the owns that have been delivered) against manufacturing defects and all installation work performed by the contractor. During this period, the contractor will be responsible for components, labor, if necessary, transportation and all other costs associated with the repair or replacement of defective components in the system. |  YES |  NO |  |
| 31 | After the expiration of the system warranty, the Supplier will be responsible only for component replacement and transportation to the GIZ office in Indonesia, but not for labor costs, during the minimum warranty periods of the key components (Battery and PV Inverter, Li-Ion Battery). Manufacturer's warranties, including modules, cooling system components, and batteries, must be in effect and transferable to end users at the time of installation. |  YES |  NO |  |

I, the undersigned, certify that I am duly authorized by [insert full name of bidder] to sign this quotation and bind [insert full name of bidder] should GIZ accept this quotation:

Name: [complete]

Title: [complete]

Date: [complete]

Signature and company stamp: _____________________________________________________________