## BoM_Solar System IPB
Bill Of Materials: Solar System IPB
Solar System EQUIPMENT (COMPONENT)
No | Category | Quantity | Item description | Specification | Picture | Unit price (IDR) | Total price (IDR) | Link
1 | Mounting system | 6 | Photovoltaic roof mounting system for 6 strings | Mounting System Type: Rail-based aluminum mounting system, suitable for pitched roofs with metal surfaces. Security (Anti-theft) screws for fixing the PV panels must be utilized. The mounting system brackets must be securely attached to the roof to be able to withstand wind loads on the mounting system. The modules and structures need to be able to support wind loads of up to 58 m/s (category 3 storms) . |  |  | 0 | https://solar.id/products/grace-solar-gs-energy-roof-mounting-system-nt-triangle-bracket
2 | Wiring and cables (DC Cables including cable termination and accessories (e.g MC4, lugs, ties ) | 70 | Solar Flex Copper Cable (m) | All necessary cables, plugs and associated materials must be included in the delivery. Insulated, stranded, flexible copper wiring should be used for DC systems. All wiring must be suitable for the intended uses and labelled as such. All cables must be double insulated, ozone, weather and UV resistant, halogen free, resistant to acid and bases. Flame retardant to DIN VDE 0482-332-1-2, DIN EN 60332-1-2. Hydrolysis and ammoniac resistant. Rodent protection and VDE, TüV, UL approved. The cross section and maximum length should follow the indications of the wiring diagrams. Cables used for the electrical connection between loads and batteries must be flexible, high conductivity copper conductors, insulated and colour coded with a general purpose PVC jacket. Connections to the battery must be made using the correct size terminals, depending on the type of battery. Field installed wiring should be terminated using terminal blocks or screw connectors. All connections must be made in watertight junction boxes. Single wires should be installed in neat, good quality conduits. Insulating materials must comply with the heat and fire resistance requirements stipulated by international standards (UTE or IEE). DC connections must have clearly labelled polarity. Cable canals need to be used for all wiring between components. Following minimum requirements must be fulfilled: Temperature Range: -40 to 90 °C Maximum Temperature at Conductor: 120 °C Short Circuit Temperature: 200 °C for up to 5 seconds Nominal Voltage (VDE): 600 / 1000 VAC / 1800 V DC conductor to conductor AC Test Voltage: 10,000 V Highest Permissible Voltage: DC: conductor/conductor 1.8 kV, conductor/earth 0.9 kV AC: conductor/earth 0.9 kV Three-phase: conductor/conductor 1.2 kV |  |  | 0 | https://shop.helukabel.com/vn-en/solarflex-x-h1z2z2-k-m713529/713531
3 | PV Combiner Box | 3 | PV Combiner Box | Number of Inputs (Strings): 2 Input Voltage Range: 200 – 1000 V DC Maximum Input Current per String: 15 A 2 × String Fuses ( 15 A ) Surge Protection Device Reverse polarity protection 1 × DC Circuit Breaker or Load Break Switch Material: Powder-coated steel or polycarbonate UV and corrosion resistant Protection Rating:IP66 Pre-installed cable glands or MC4 connectors Operating Temperature: -25 °C to +60 °C Mounting: Wall-mounted |  |  | 0 | https://voltaconsolar.com/products/pv-combiner-box-2way-in-2way-out?_gl=1*1biwxx1*_up*MQ..*_ga*NjM1OTExNjUyLjE3NTMzMDQxMjQ.*_ga_DFK101QW8E*czE3NTMzMDQxMjMkbzEkZzAkdDE3NTMzMDQxMjMkajYwJGwwJGgyMDI0Mzc4NjA0
4 | Energy Meter | 3 | Energy Meter For monitoring energy consumption. | 230 V AC 1 Phase Modbus TCP type. Open register suitable for PCL systems Up to 25 A |  |  | 0 | https://verkauf-bochum.de/products/energy-meter-vm-3p75ct-3-phase-max-65a-phase?variant=44768865648907&currency=EUR&trc_gcmp_id=18267938341&gad_source=1&gad_campaignid=17417392263&gbraid=0AAAAAoSF8ZsJvKDg218hf2NKHwHlQXZlZ&gclid=Cj0KCQjwkILEBhDeARIsAL--pjxxzRNMgqPyz-KWDwOghy_WzclwuRebWfCaTrjvO4KDEhf4jEwKEK8aAsZhEALw_wcB
5 | Batteries | 6 | Battery | Lithium-Ion Type LiFePO4 48 V DC batteries Wall mounted type. The batteries need to be compatible with the off-grid inverter Non-Toxic & Non-Hazardous Cobalt-Free LFP Chemistry with Built-In Safety Battery Management System is mandatory. CAN communication interface, integrated circuit-breaker and IP65 waterproof is mandatory. The number of batteries is specified in Annex 1 for each site. The batteries must be connected in parallel. Positive and negative polarity must be clearly indicated. Each battery must be labelled with at least: Manufacturer, type, model number, voltage rating, capacity, and year of manufacture. Compliance with EN IEC 61000-6-2:2019, IEC 62619:2017, ICE63056:2020 and VDE-AR- 2510-50:2017 is required. Compliance with CE is mandatory. Voltage Range: 44.5 - 59 V DC Rated Capacity: 4.75 - 5.25 kWh Peak Current: 135 - 250 A DC Continuous Charge Current: 80 - 150 A DC Efficiency: 96 - 98% Operation Temperature: 0 - 45 °C Relative Humidity Range: 5 - 95% Number of Cycles: 6,000 at 80% DOD |  |  | 0 | https://www.energy-xprt.com/products/bslbatt-model-b-lfp48-250pw-home-battery-backup-power-supply-lifepo4-48v-100ah-5kwh-lithium-battery--835728
6 | Battery Fuses | 5 | DC Fuse | 15A |  |  | 0 | https://www.reichelt.de/de/de/shop/produkt/kfz-sicherung_normoto_15_a_blau-242052?PROVID=2788&gad_source=1&gad_campaignid=1622074784&gbraid=0AAAAADwnxtZZ4hRtlF6J4xaqwUNnHZPlP&gclid=Cj0KCQjwkILEBhDeARIsAL--pjwbA8NMNldUVE6nz6I5FAywPNyXcFuH6f96BOFCldmRZnbJRguQD40aAs6NEALw_wcB
7 | Main Box | 1 | Main switch board box | IP 54 |  |  | 0 | https://www.alibaba.com/product-detail/IP54-Outdoor-MCCB-Electrical-Main-Switch_60267589984.html
8 | SPD | 12 | DC Surge Protection Device (SPD) | Type 1,2 and 3 (AC and DC based on wiring diagram) |  |  | 0 | https://www.surge-protectiondevice.com/sale-14184968-type-1-2-3-25ka-275v-spd-2-poles-type-1-surge-protector-lightning-protection.html
9 | RCD | 2 | Residual Current Device (RCD) | Connected to various MCBs based on wiring diagram |  |  | 0 | https://www.rs-online.id/p/rcd-40-4-003-a/
10 | Fuse | 2 | Battery Fuse | 200A |  |  | 0 | https://auprotec.de/de/elektrik/sicherungshalter/sicherungshalter-fuer-mega-sicherungen-mit-schutzabdeckung-mega-sicherung-200a-blau/p/006041?gad_source=1&gad_campaignid=17432427010&gbraid=0AAAAADRLiNUmaZcS3Tmavk0FM3IUPJU09&gclid=Cj0KCQjwkILEBhDeARIsAL--pjyXr5s2t9UoIzPbdyQUnEmu2WVBMlg2VOqQv4Ljhc9Qn1EUBT701CoaAvDQEALw_wcB&_fc_state=0
11 | MCB | 20 | Miniature Circuit Breaker (MCB) | 6A, 16A, 20A, 40A; Type C; DP AC output/input based on wiring diagram: IEC 60947-2 Compliance |  |  | 0 | https://tameson.com/products/schneider-electric-merlin-gerin-circuit-breaker-r9p19610-e27d2
12 | Busbar | 2 | Busbar | L busbar, N busbar; 25mm x 3mm |  |  | 0 | https://verkauf-bochum.de/products/busbar-150a-4p-cover?variant=44568684232971&currency=EUR&trc_gcmp_id=18267938341&gad_source=1&gad_campaignid=17417392263&gbraid=0AAAAAoSF8ZsJvKDg218hf2NKHwHlQXZlZ&gclid=Cj0KCQjwkILEBhDeARIsAL--pjzSgJcidbX0c9WiJnDaqsEqQW4som_v5jYPQs5CNh3Hb7XUr9be78AaAiYWEALw_wcB
13 | Switch | 4 | Isolator Switch | For various AC input/output paths 230 V AC according wiring diagramm |  |  | 0
14 | AC/DC Converter | 1 | AC/DC Converter | Input 230V AC Output 24 VDC |  |  | 0 | https://www.automation24.de/schaltnetzteil-phoenix-1088495-step3-ps-1ac-24dc-0-63-pt?previewPriceListId=8&gad_source=1&gad_campaignid=21166870019&gbraid=0AAAAADnTuz__-0IuMuEo-vTVDJ2w64Q1b&gclid=Cj0KCQjwkILEBhDeARIsAL--pjwGzIpi8zhOGlqAPTN0plABev4qJBMkVJfIPlV2WogmOCoRV4fVk4IaAn0mEALw_wcB
15 | AC Cables and installation materials | 1 | Conduits, trays, ducts, clips, ties, glands, and junction boxes | According to wiring diagram, |  |  | 0 | https://www.plica.ch/en/unex-kabelkanal-und-kabeltrasse/
16 | Inverter | 3 | PV Inverter | PV generator power: 7,500 Wp. Maximum input voltage: 600 V. MPP voltage range: 140 V – 500 V. Max. input current per MPPT: 15 A. Number of MPP trackers: 2. Rated AC power: 4,000 kVA Nominal AC voltage: 230 V. AC frequency: 50 Hz. Max. output current: 22 A. Efficiency: 97.0 %. Protection rating: IP65. Communication protocols: Modbus TCP (Preferable SMA Sunny Boy 4.0 due to a current cooperation with one of our partners) |  |  | 0 | https://www.rasuni.com/products/sma-sunny-boy-4-0?pr_prod_strat=e5_desc&pr_rec_id=c4322d0f9&pr_rec_pid=1903221407795&pr_ref_pid=8714464231752&pr_seq=uniform
17 | Inverter | 1 | Off-Grid Battery Inverter | AC Input Power : 11,500 kVA Off-Grid AC Power (at 25 °C): 6,000 kVA (continuous), 8,000 kVA for 30 minutes, 11,000 kVA for 3 seconds AC Voltage (Output): 230 V ± 2% AC Frequency: 50/60 Hz (automatic detection) Battery Voltage Range: 41 V to 63 V Efficiency: 95.8% Protection Class: IP54 Cooling: Temperature-controlled fan Communication protocols: Modbus TCP (Preferable SMA Sunny Island 8.0 due to a current cooperation with one of our partners) |  |  | 0 | https://www.rasuni.com/products/sma-sunny-island-8-0h-si8-0h-13?_pos=1&_sid=d5a080d62&_ss=r
18 | Energy Meter | 2 | Inverter Energy Meter | For assuring net-zero energy balance at grid point (conected and compatible to the selected PV inverters) - Connection to the local router via Ethernet cable (10/100 Mbit/s, RJ45 plug) - Inputs (voltage and current): Nominal voltage 230 V/400 V Frequency 50 Hz/±5% Nominal current / limiting current per line conductor 5 A/63 A (>63 A can be connected via external current transformers) Start-up current < 25 mA - Protection class (according to IEC 62103) II - Degree of protection (according to IEC 60529) IP2X |  |  | 0 | https://www.rasuni.com/products/sma-energy-meter-2-0?_pos=1&_sid=5a8ce9024&_ss=r
19 | Weather station including Irradiance sensor and temperature | 1 | Pyranometer | ISO 9060 spectrally flat Class C 0 to 1 Volt or 4 to 20 mA analogue output No change of desiccant for 10 years Active temperature correction from -40 °C to +80 °C temperature response < 5 % (-10 °C to +40 °C) |  |  | 0 | Smart Pyranometer SMP3 - Kipp & Zonen
[6 empty] | 1. Solar System EQUIPMENT (COMPONENT) | 0
Materials availailable onsite at IPB and not part of the delivery of the contractor
No | Category | Quantity | Item description | Specification | Picture | Unit price | Total price | Link
1 | PV Modules | 42 | Solar PV Module | 405Wp per module |  | already provided | already provided
MANPOWER (subject to income tax) Consist of: a) Expert fee b) Travel Expenses (transport, accommodation and daily allowance) c) Income tax included
No | Category | Quantity | Item description | Specification | Picture | Unit price | Total price | Link
2 | Engineering | 1 | - Project Management (include as build drawing) - Permit and regulation compliance (NIDI, PLN Application, IUPTLS, SLO) |  |  |  | 0
3 | Installation | 1 | - Installation and commissioning, training post installation. |  |  |  | 0
4 | Maintenance | 1 | 2 times regular maintenance (at 6 and 12 month after installation) |  |  |  | 0
[6 empty] | TOTAL SERVICE | 0
Delivery cost
No | Category | Quantity | Item description | Specification |  | Unit price | Total price | Link
5 | Delivery cost | 1 | Transport of the equipment | Charges DAP to site IPB Bogor |  |  | 0
[6 empty] | TOTAL SERVICE | 0

## Bid Price Form
PRICE SCHEDULE FORM
Bidders shall fill in this Price Schedule Form in accordance with the instructions indicated.
| Ref. Tender No: |  | 91189746
Supplier Name :
Supplier Address :
Area Code, City:
Telephone:
Email:
| No. | Item Description | Specification | Quantity | Unit | Unit price (IDR) | Total amount (IDR) | Remarks
| A. |  | the specification as stipulated in the Technical Specification Form (as integral part of this Bid Price Form)
| 1 | Solar System EQUIPMENT (COMPONENT) |  | 1 | package | 0 | 0
| 2 | Engineering (subject to income tax) |  | 1 | package | 0 | 0 | subject to income tax
| 3 | Installation (subject to income tax) |  | 1 | package | 0 | 0
| 4 | Maintenance (subject to income tax) |  | 1 | package | 0 | 0
| 5 | Delivery cost (subject to income tax) |  | 1 | package | 0 | 0
0
[5 empty] | Sub Total |  | 0
| Note : The Value Added Tax of 11% will be exempted |  |  |  | VAT 11% |  | 0
| GRAND TOTAL | [5 empty] | 0
Terms and Conditions :
1. All prices/rates quoted must be exclusive of all taxes, since the GIZ, including its subsidiary organs, is exempt from taxes.
2. GIZ shall process the VAT with tax exemption (08) to BADORA. The The process of tax exemption will take 2 - 3 months
3. This bid price form must be protected with password to secure your bid price proposal.
4. Please make sure to save the password. The change of password may cause your bid will not be considered.
5. The price shall be valid for 100 days commencing on the date of submission of quotation
6. The price shall include the packaging
7. Self Declaration of Annex 3 and Annex 4 shall be signed and attached with the tender documents
8. General Terms of conditions as Annex 3 of this Bid Form
I, the undersigned, certify that I am duly authorized by [insert full name of Bidder] to sign this quotation and bind [insert full name of Bidder] should GIZ accept this quotation:
| Name |  | : _____________________________________________________________
| Title |  | : _____________________________________________________________
| Date |  | : _____________________________________________________________
| Signature and Company Stamp |  | : _____________________________________________________________