## Specifications
SPECIFICATIONS
Item | Specification | Picture
new mechanical water meters (complete with gaskets or O-rings) DN 25 mm | 1. Meter registers shall be marked in the metric system with the litre as the smallest unit of measurement
2. All the meters shall be fitted with screwed connections or be flanged. Flanged meters to be supplied complete with gasket sets.
3. Technical product literature with detailed specifications must be provided together with the returned tender documentation.
4. Calibration or verification certificates by an accredited laboratory must be provided.
5. Meters must fully comply with South African National Standards (SANS) 1529-1/SANS 1529-9, class B or C.
6. The meter body must be manufactured from composite material based on a polymer with glass fibres.
7. The registers (dry dial only) must be hermetically sealed copper/glass canned construction in compliance with IP68 standards ensuring a waterproof enclosure. No wet dial meters may be provided.
8. Loose pre-calibrated measuring inserts to be supplied complete with registers, O-rings and/or appropriate sealing gaskets.
9. Registers should have the facility for providing outputs (which should include at least one digital pulse), for connecting to third-party Global System for Mobile Communications (GSM) enabled data logging systems for remote data acquisition and assessment.
10. All meters must be capable of accepting pre-calibrated measuring inserts without loss of accuracy.
11. All cover bolts must be stainless steel to ensure ease of maintenance.
12. All meters must be capable of withstanding a nominal working pressure of at least 1600 kPa.
13. Meters should maintain their accuracy when installed in an inclined, vertical or horizontal plane.
14.Reed switches / pulsers should have an open-ended fly lead of at least 0.5m long. All reed switches / pulsers shall be original as specified by the manufacturer. No after market reed switches / pulsers will be allowed. The pulse output shall be at least 1m3.
15. All manufacturer’s warranties must be handed to the municipality. A warranty of 12 months against any defects in materials and workmanship shall be provided for all items tendered.
new mechanical water meters (complete with gaskets or O-rings) DN 40 mm | 1. Meter registers shall be marked in the metric system with the litre as the smallest unit of measurement | #VALUE!
2. All the meters shall be fitted with screwed connections or be flanged. Flanged meters to be supplied complete with gasket sets.
3. Technical product literature with detailed specifications must be provided together with the returned tender documentation.
4. Calibration or verification certificates by an accredited laboratory must be provided.
5. Meters must fully comply with SANS 1529-1/SANS 1529-9, class B or C.
6. The meter body must be manufactured from cast iron and powder coated with a fusion bonded epoxy to a minimum dry thickness of 150 microns.
7. The registers (dry dial only) must be hermetically sealed copper/glass canned construction in compliance with IP68 standards ensuring a waterproof enclosure. No wet dial meters may be provided.
8. Loose pre-calibrated measuring inserts to be supplied complete with registers, O-rings and/or appropriate sealing gaskets.
9. Registers should have the facility for providing outputs (which should include at least one digital pulse), for connecting to third-party GSM enabled data logging systems for remote data acquisition and assessment.
10. All meters must be capable of accepting pre-calibrated measuring inserts without loss of accuracy.
11. All cover bolts must be stainless steel to ensure ease of maintenance.
12. All meters must be capable of withstanding a nominal working pressure of at least 1600 kPa.
13. DN40 meters must be flanged to SANS 1123 Table 16 (or BS4504 / EN1092-1, PN16), or threaded (2” BSP).
14. Meters should maintain their accuracy when installed in an inclined, vertical or horizontal plane.
15.Reed switches / pulsers should have an open-ended fly lead of at least 0.5m long. All reed switches / pulsers shall be original as specified by the manufacturer. No after market reed switches / pulsers will be allowed. The pulse output shall be at least 1m3.
16. All manufacturer’s warranties must be handed to the municipality. A warranty of 12 months against any defects in materials and workmanship shall be provided for all items tendered.
new mechanical water meters (complete with gaskets or O-rings) DN 50 mm | 1. Meter registers shall be marked in the metric system with the litre as the smallest unit of measurement | #VALUE!
2. All the meters shall be fitted with screwed connections or be flanged. Flanged meters to be supplied complete with gasket sets.
3. Technical product literature with detailed specifications must be provided together with the returned tender documentation.
4. Calibration or verification certificates by an accredited laboratory must be provided.
5. Meters must fully comply with SANS 1529-1/SANS 1529-9, class B or C.
6. The meter body must be manufactured from cast iron and powder coated with a fusion bonded epoxy to a minimum dry thickness of 150 microns.
7. The registers (dry dial only) must be hermetically sealed copper/glass canned construction in compliance with IP68 standards ensuring a waterproof enclosure. No wet dial meters may be provided.
8. Loose pre-calibrated measuring inserts to be supplied complete with registers, O-rings and/or appropriate sealing gaskets.
9. Registers should have the facility for providing outputs (which should include at least one digital pulse), for connecting to third-party GSM enabled data logging systems for remote data acquisition and assessment.
10. All meters must be capable of accepting pre-calibrated measuring inserts without loss of accuracy.
11. All cover bolts must be stainless steel to ensure ease of maintenance.
12. All meters must be capable of withstanding a nominal working pressure of at least 1600 kPa.
13. Meters must be flanged to SANS 1123 Table 16 (or BS4504 / EN1092-1, PN16).
14. Meters should maintain their accuracy when installed in an inclined, vertical or horizontal plane.
15.Reed switches / pulsers should have an open-ended fly lead of at least 0.5m long. All reed switches / pulsers shall be original as specified by the manufacturer. No after market reed switches / pulsers will be allowed. The pulse output shall be at least 1m3.
16. All manufacturer’s warranties must be handed to the municipality. A warranty of 12 months against any defects in materials and workmanship shall be provided for all items tendered.
new mechanical water meters (complete with gaskets or O-rings) DN 80 mm | 1. Meter registers shall be marked in the metric system with the litre as the smallest unit of measurement | #VALUE!
2. All the meters shall be fitted with screwed connections or be flanged. Flanged meters to be supplied complete with gasket sets.
3. Technical product literature with detailed specifications must be provided together with the returned tender documentation.
4. Calibration or verification certificates by an accredited laboratory must be provided.
5. Meters must fully comply with SANS 1529-1/SANS 1529-9, class B or C.
6. The meter body must be manufactured from cast iron and powder coated with a fusion bonded epoxy to a minimum dry thickness of 150 microns.
7. The registers (dry dial only) must be hermetically sealed copper/glass canned construction in compliance with IP68 standards ensuring a waterproof enclosure. No wet dial meters may be provided.
8. Loose pre-calibrated measuring inserts to be supplied complete with registers, O-rings and/or appropriate sealing gaskets.
9. Registers should have the facility for providing outputs (which should include at least one digital pulse), for connecting to third-party GSM enabled data logging systems for remote data acquisition and assessment.
10. All meters must be capable of accepting pre-calibrated measuring inserts without loss of accuracy.
11. All cover bolts must be stainless steel to ensure ease of maintenance.
12. All meters must be capable of withstanding a nominal working pressure of at least 1600 kPa.
13. Meters must be flanged to SANS 1123 Table 16 (or BS4504 / EN1092-1, PN16).
14. Meters should maintain their accuracy when installed in an inclined, vertical or horizontal plane.
15.Reed switches / pulsers should have an open-ended fly lead of at least 0.5m long. All reed switches / pulsers shall be original as specified by the manufacturer. No after market reed switches / pulsers will be allowed. The pulse output shall be at least 1m3.
16. All manufacturer’s warranties must be handed to the municipality. A warranty of 12 months against any defects in materials and workmanship shall be provided for all items tendered.
new mechanical water meters (complete with gaskets or O-rings) DN 100 mm | 1. Meter registers shall be marked in the metric system with the litre as the smallest unit of measurement | #VALUE!
2. All the meters shall be fitted with screwed connections or be flanged. Flanged meters to be supplied complete with gasket sets.
3. Technical product literature with detailed specifications must be provided together with the returned tender documentation.
4. Calibration or verification certificates by an accredited laboratory must be provided.
5. Meters must fully comply with SANS 1529-1/SANS 1529-9, class B or C.
6. The meter body must be manufactured from cast iron and powder coated with a fusion bonded epoxy to a minimum dry thickness of 150 microns.
7. The registers (dry dial only) must be hermetically sealed copper/glass canned construction in compliance with IP68 standards ensuring a waterproof enclosure. No wet dial meters may be provided.
8. Loose pre-calibrated measuring inserts to be supplied complete with registers, O-rings and/or appropriate sealing gaskets.
9. Registers should have the facility for providing outputs (which should include at least one digital pulse), for connecting to third-party GSM enabled data logging systems for remote data acquisition and assessment.
10. All meters must be capable of accepting pre-calibrated measuring inserts without loss of accuracy.
11. All cover bolts must be stainless steel to ensure ease of maintenance.
12. All meters must be capable of withstanding a nominal working pressure of at least 1600 kPa.
13. Meters must be flanged to SANS 1123 Table 16 (or BS4504 / EN1092-1, PN16).
14. Meters should maintain their accuracy when installed in an inclined, vertical or horizontal plane.
15.Reed switches / pulsers should have an open-ended fly lead of at least 0.5m long. All reed switches / pulsers shall be original as specified by the manufacturer. No after market reed switches / pulsers will be allowed. The pulse output shall be at least 1m3.
16. All manufacturer’s warranties must be handed to the municipality. A warranty of 12 months against any defects in materials and workmanship shall be provided for all items tendered.
new mechanical water meters (complete with gaskets or O-rings) DN 150 mm | 1. Meter registers shall be marked in the metric system with the 10 litre as the smallest unit of measurement indicated on the dial of meters | #VALUE!
2. The meters shall be fitted with screwed connections or be flanged. Flanged meters to be supplied complete with gasket sets.
3. Technical product literature with detailed specifications must be provided together with the returned tender documentation.
4. Calibration or verification certificates by an accredited laboratory must be provided.
5. Meters must fully comply with SANS 1529-4/SANS 1529-9, class B or C, OR International Organization of Legal Metrology (OIML) R49-1.
6. The meter body must be manufactured from cast iron and powder coated with a fusion bonded epoxy to a minimum dry thickness of 150 microns.
7. The registers (dry dial only) must be hermetically sealed copper/glass canned construction in compliance with IP68 standards ensuring a waterproof enclosure. No wet dial meters may be provided.
8. Loose pre-calibrated measuring inserts to be supplied complete with registers, O-rings and/or appropriate sealing gaskets.
9. Registers should have the facility for providing outputs (which should include at least one digital pulse), for connecting to third-party GSM enabled data logging systems for remote data acquisition and assessment.
10. All meters must be capable of accepting pre-calibrated measuring inserts without loss of accuracy.
11. All cover bolts must be stainless steel to ensure ease of maintenance.
12. All meters must be capable of withstanding a nominal working pressure of at least 1600 kPa.
13. Meters must be flanged to SANS 1123 Table 16 (or BS4504 / EN1092-1, PN16).
14. Meters should maintain their accuracy when installed in an inclined, vertical or horizontal plane.
15.Reed switches / pulsers should have an open-ended fly lead of at least 0.5m long. All reed switches / pulsers shall be original as specified by the manufacturer. No after market reed switches / pulsers will be allowed. The pulse output shall be at least 1m3.
16. All manufacturer’s warranties must be handed to the municipality. A warranty of 12 months against any defects in materials and workmanship shall be provided for all items tendered.
new water meter mechanism (complete with new gasket or O-ring) for existing meters DN 50mm | Woltman Dynamic (WPD) meter mechanism | #VALUE!
new water meter mechanism (complete with new gasket or O-ring) for existing meters DN 150mm | Meistream meter mechanism | #VALUE!
new water meter mechanism (complete with new gasket or O-ring) for existing meters DN 150mm | Woltman Dynamic (WPD) meter mechanism | #VALUE!
new water meter mechanism (complete with new gasket or O-ring) for existing meters DN 200mm | Meistream meter mechanism | #VALUE!
new water meter mechanism (complete with new gasket or O-ring) for existing meters DN 225mm | Woltman Dynamic (WPD) meter mechanism | #VALUE!
new water meter mechanism (complete with new gasket or O-ring) for existing meters DN 250mm | Woltman Dynamic (WPD) meter mechanism | #VALUE!
new water meter mechanism (complete with new gasket or O-ring) for existing meters DN 300mm | Woltman Dynamic (WPD) meter mechanism | #VALUE!
new electromagnetic water meters (battery operated, remote sensor) (complete with gaskets or O-rings) DN 250mm | 1. Meter registers shall be marked in the metric system with the 10 litre being the smallest unit of measurement indicated on the dial of meters.
2. Meters shall be fitted with screwed connections or be flanged. Flanged meters to be supplied complete with gasket sets.
3. Technical product literature with detailed specifications must be provided together with the returned tender documentation.
4. Calibration or verification certificates by an accredited laboratory must be provided.
5. Must fully comply with SANS 1529-4/SANS 1529-9, class B or C, OR OIML R49-1 (accuracy class 2).
6. Electronics and battery pack enclosure to be IP 67 compatible, with minimum cable length between sensor tube and discrete electronics to be 20m.
7. Bi-directional flow outputs and totalisation to be provided.
8. Empty pipe detection facility.
9. The sensor tube should be sealed in compliance with IP68 standards and should be able to operate in fully submerged conditions.
10. Battery/battery pack to be field replaceable.
11. Meters should have the facility for providing outputs (which should include at least one digital pulse), for connecting to third-party GSM enabled data logging systems for remote data acquisition and assessment.
12. When digital pulse outputs are used, the minimum battery lifetime should be 10 years in conditions with ambient temperatures ranging from 50C to 450C.
13. Meters must be capable of withstanding a nominal working pressure of at least 1600 kPa.
14. Meters must be flanged to SANS 1123 Table 16 (or BS4504 / EN1092-1 PN16),
15. Meters should maintain their accuracy when installed in an inclined, vertical or horizontal plane.
16. All manufacturer’s warranties must be handed to the municipality. A warranty of 12 months against any defects in materials and workmanship shall be provided for all items tendered.
new electromagnetic water meters (battery operated, remote sensor) (complete with gaskets or O-rings) DN 300mm | 1. Meter registers shall be marked in the metric system with the 10 litre being the smallest unit of measurement indicated on the dial of meters.
2. Meters shall be fitted with screwed connections or be flanged. Flanged meters to be supplied complete with gasket sets.
3. Technical product literature with detailed specifications must be provided together with the returned tender documentation.
4. Calibration or verification certificates by an accredited laboratory must be provided.
5. Must fully comply with SANS 1529-4/SANS 1529-9, class B or C, OR OIML R49-1 (accuracy class 2).
6. Electronics and battery pack enclosure to be IP 67 compatible, with minimum cable length between sensor tube and discrete electronics to be 20m.
7. Bi-directional flow outputs and totalisation to be provided.
8. Empty pipe detection facility.
9. The sensor tube should be sealed in compliance with IP68 standards and should be able to operate in fully submerged conditions.
10. Battery/battery pack to be field replaceable.
11. Meters should have the facility for providing outputs (which should include at least one digital pulse), for connecting to third-party GSM enabled data logging systems for remote data acquisition and assessment.
12. When digital pulse outputs are used, the minimum battery lifetime should be 10 years in conditions with ambient temperatures ranging from 50C to 450C.
13. Meters must be capable of withstanding a nominal working pressure of at least 1600 kPa.
14. Meters must be flanged to SANS 1123 Table 16 (or BS4504 / EN1092-1 PN16),
15. Meters should maintain their accuracy when installed in an inclined, vertical or horizontal plane.
16. All manufacturer’s warranties must be handed to the municipality. A warranty of 12 months against any defects in materials and workmanship shall be provided for all items tendered.
new ball isolating valves DN 40 mm | 1. Shall be Ball Lever Type screwed British Standard Pipe (BSP) female x female or female X male. Body: Brass with Nickel-plated. Ball: Stainless steel. Seats: Polytetrafluoroethylene (PTFE). Handle: stainless steel or Nickel-plated. | #VALUE!
2. Face-to-face dimension shall be in accordance with SANS 664/SANS 191.
3. The valve body shall incorporate a straight unobstructed body passage without pockets and shall have inclined seats to eliminate deposits in the valve body.
4. Gate shall be fully encapsulated with drinking water approved EPDM rubber.
5. The gate guides/shoes shall be manufactured using wear resistant Nylon.
6. Shaft material shall be stainless steel 431.
7. Coating shall be 250 microns fusion bonded epoxy or two pack epoxy coated, RAL 5015 European color standard system (Reichs-Ausschuss für Lieferbedingungen). Colour blue
8. Operation shall be by hand wheel or cap top, clockwise to close as standard orientation.
9. Maximum operating temperature shall be 70°C.
10. All manufacturer’s warranties must be handed to the municipality. A warranty of 12 months against any defects in materials and workmanship shall be provided for all items tendered.
new isolating valves 50mm Resilient Seated Valve (RSV) isolating valve | 1. Shall be a resilient seal, non-rising spindle type in ductile cast iron with flanged or socketed end connections. | #VALUE!
2. Face-to-face dimension shall be in accordance with SANS 664/SANS 191.
3. The valve body shall incorporate a straight unobstructed body passage without pockets and shall have inclined seats to eliminate deposits in the valve body.
4. Gate shall be fully encapsulated with drinking water approved Ethylene Propylene Diene Monomer (EPDM) rubber.
5. The gate guides/shoes shall be manufactured using wear resistant Nylon.
| 6. Shaft material shall be stainless steel 431. | #VALUE!
7. Coating shall be 250 microns fusion bonded epoxy or two pack epoxy coated, RAL 5015. Colour blue
8. Operation shall be by hand wheel or cap top, clockwise to close as standard orientation.
9. Maximum operating temperature shall be 70°C.
10. All manufacturer’s warranties must be handed to the municipality. A warranty of 12 months against any defects in materials and workmanship shall be provided.
new isolating valves 100mm Resilient Seated Valve (RSV) isolating valve | 1. Shall be a resilient seal, non-rising spindle type in ductile cast iron with flanged or socketed end connections. | #VALUE!
2. Face-to-face dimension shall be in accordance with SANS 664/SANS 191.
3. The valve body shall incorporate a straight unobstructed body passage without pockets and shall have inclined seats to eliminate deposits in the valve body.
4. Gate shall be fully encapsulated with drinking water approved Ethylene Propylene Diene Monomer (EPDM) rubber.
5. The gate guides/shoes shall be manufactured using wear resistant Nylon.
| 6. Shaft material shall be stainless steel 431. | #VALUE!
7. Coating shall be 250 microns fusion bonded epoxy or two pack epoxy coated, RAL 5015. Colour blue
8. Operation shall be by hand wheel or cap top, clockwise to close as standard orientation.
9. Maximum operating temperature shall be 70°C.
10. All manufacturer’s warranties must be handed to the municipality. A warranty of 12 months against any defects in materials and workmanship shall be provided.
new isolating valves 250mm Resilient Seated Valve (RSV) isolating valve | 1. Shall be a resilient seal, non-rising spindle type in ductile cast iron with flanged or socketed end connections. | #VALUE!
2. Face-to-face dimension shall be in accordance with SANS 664/SANS 191.
3. The valve body shall incorporate a straight unobstructed body passage without pockets and shall have inclined seats to eliminate deposits in the valve body.
4. Gate shall be fully encapsulated with drinking water approved Ethylene Propylene Diene Monomer (EPDM) rubber.
5. The gate guides/shoes shall be manufactured using wear resistant Nylon.
| 6. Shaft material shall be stainless steel 431. | #VALUE!
7. Coating shall be 250 microns fusion bonded epoxy or two pack epoxy coated, RAL 5015. Colour blue
8. Operation shall be by hand wheel or cap top, clockwise to close as standard orientation.
9. Maximum operating temperature shall be 70°C.
10. All manufacturer’s warranties must be handed to the municipality. A warranty of 12 months against any defects in materials and workmanship shall be provided.
new isolating valves 300mm Resilient Seated Valve (RSV) isolating valve | 1. Shall be a resilient seal, non-rising spindle type in ductile cast iron with flanged or socketed end connections. | #VALUE!
2. Face-to-face dimension shall be in accordance with SANS 664/SANS 191.
3. The valve body shall incorporate a straight unobstructed body passage without pockets and shall have inclined seats to eliminate deposits in the valve body.
4. Gate shall be fully encapsulated with drinking water approved Ethylene Propylene Diene Monomer (EPDM) rubber.
5. The gate guides/shoes shall be manufactured using wear resistant Nylon.
| 6. Shaft material shall be stainless steel 431. | #VALUE!
7. Coating shall be 250 microns fusion bonded epoxy or two pack epoxy coated, RAL 5015. Colour blue
8. Operation shall be by hand wheel or cap top, clockwise to close as standard orientation.
9. Maximum operating temperature shall be 70°C.
10. All manufacturer’s warranties must be handed to the municipality. A warranty of 12 months against any defects in materials and workmanship shall be provided.