## BOM-Technical Specification
ANNEX 1. – TECHNICAL SPECIFICATION FORM TENDER No. 10019816
Bidders are requested to complete this form, sign it and return it as part of their bid submission. The bidder shall fill in this form in accordance with the instructions indicated. No alterations to its format shall be permitted and no substitutions shall be accepted.
This technical specification form has an integral part with the Bid Price Form for this tender.
Date: [Insert submission date]
Name of the Bidder: [Insert the company name]
Subject: Procurement and Installation of Solar PV for KNMP Biak, Inquiry 10019816 dated 28.07.2026
No | Category | Item description | Specification | Quantity | Unit | Applicable TRs (Based on TOR) | Condensed TR compliance | Note
A | Solar PV system
1 | PV Modules | PV Module | Tier 1 and N-Type HPBC bifacial photovoltaic modules suitable for rooftop and canopy installation. Minimum nameplate power ≥650 Wp and minimum efficiency ≥24% under STC. Factory-fitted IP68 junction box with bypass diodes. Supplied with MC4-type or equivalent connectors, IP68 when mated. IEC 61215 and IEC 61730 certified. Unique serial number traceability required. Suitable for coastal/marine environment with high humidity and salt mist. | 86.45 | kWp | TR-PV-01–09 | ≥650 Wp crystalline Si, ≥24%, IEC certified, IP68 J-box
2 | Inverters | PV inverters | Three-phase string inverter suitable for microgrid operation, 230/400 V, 50 Hz AC system, and AC-coupled PV-battery application. The total inverter AC capacity shall be selected with a DC/AC ratio not exceeding 1.15. Compatible with PV string design up to 1,000 Vdc. Minimum three (3) independent MPPTs per inverter to minimize the mismatch losses. European efficiency ≥ 98%. The inverter shall include integrated DC disconnection. Outdoor enclosure protection of at least IP65. The manufacturer shall have experience in Indonesia within the last three years. The PV inverter shall be of the same manufacturer as the battery inverter to ensure that PV inverter is fully compatible with the proposed battery inverter. | 3 | pcs | TR-INV-01–13 | 3ph PV inverter, ≥98%
B | Battery Energy Storage System (BESS)
3 | Battery | LFP battery packs including the EMS | Lithium Iron Phosphate (LFP) battery chemistry Minimum installed energy capacity: 150 kWh Minimum usable energy capacity: 120 kWh Modular stacking-type architecture with balanced parallel battery strings Minimum continuous charge/discharge rate: 0.5C Minimum design life: 6,000 cycles at 80% Depth of Discharge (DoD) Nominal DC voltage range suitable for integration with battery inverter systems used in islanded and grid-connected microgrids Integrated Battery Management System (BMS) with cell-level monitoring and balancing State of Charge (SoC), State of Health (SoH), temperature, voltage, current, and alarm monitoring Integrated DC protection, including overcurrent, overvoltage, undervoltage, short-circuit, and reverse polarity protection Emergency isolation and remote shutdown functionality Fire and smoke detection system integrated within the battery enclosure Thermal management system designed for continuous operation under tropical environmental conditions Protection rating not less than IP65 for outdoor installation Corrosion resistance rating not less than C5-M in accordance with ISO 12944 or equivalent Communication interfaces supporting integration with battery inverters, microgrid controllers, SCADA systems, and energy management systems through open communication protocols Fully compatible with grid-forming battery inverter systems and hybrid renewable energy microgrid operation in both grid-connected and islanded modes, mandatory IEC 62619 and minimum 10-year warranty | 150 | kWh | TR-BESS-1 - 10 | LFP battery, ≥6,000 cycles, IEC62619, C= 0.5, IP65, C5
4 | Inverters | Battery inverter | Grid-forming inverter suitable for AC-coupled PV-battery operation in a 230/400 V, 50 Hz three-phase system. The battery inverter system shall consist of multiple single-phase inverter units arranged to form a three-phase network, with one or more units per phase for redundancy. The units shall be equally distributed across the three phases. The inverter shall be compatible with the proposed battery system, with nominal battery voltage of 48 V DC or as required by the selected battery. The total rated continuous AC output power shall be not less than 45 kW at the site ambient temperature of 35°C, with overload capability of at least 130% for 30 minutes and 180% for minimum 3 seconds to support high inrush current. The inverter shall have efficiency of not less than 95%, enclosure protection of at least IP54. The manufacturer shall have operational experience in Indonesia within the last three years. | 1 | lot | TR-INV-09 - 13 | Battery inverter
5 | AC Combiner | Inverter AC combiner box | The Inverter AC Combiner Box shall be suitable for combining multiple single-phase battery inverter units into a common 230/400 V, 50 Hz three-phase AC system. The combiner box capacity shall be selected to suit the PV inverter capacity, battery inverter capacity, and minimum load requirement of 45 kW. It shall include suitable protection devices for the battery inverter, PV inverter, and load connections, and shall be compatible with TN-S, TN-C-S, or TT earthing arrangements. The enclosure protection shall be not less than IP54. The Contractor shall submit manufacturer confirmation that the combiner box is approved for the proposed battery inverter model and quantity, PV inverter connection, and load connection. | 1 | set | TR-AC-06 | AC combiner box for multi-inverter microgrid
6 | AC Combiner | Automatic transfer switch system | Automatic transfer switch system (ATS) for interfacing the battery inverter / Inverter AC Combiner box with the utility grid. The equipment shall be compatible with the selected inverter system and shall provide the required connection, disconnect, and transfer function between the off-grid and the utility grid. The enclosure shall be minimum IP54, corrosion resistant, and suitable for tropical environmental conditions | 1 | set | TR-AC-07 | Automatic transfer switch system
7 | Communciation | Communiaction accessories | Complete communication, monitoring, control, and supervisory system between PV inverter, battery inverter, and battery and required other equipment to ensure a smooth operation of microgrid | 1 | set | TR-INV-11 | Inverter compatible communication accessories
C | PV Mounting (Building and Canopy Baywak )
8 | PV Mounting for building | Rooftop PV mounting structure | Complete PV mounting system for rooftop application, minimum 25-year design life, aluminum structure minimum AL6005-T5 or equivalent, SS316 fasteners, corrosion protection suitable for C5 marine environment, watertight roof penetrations where applicable, and structural design compliant with site wind/seismic loads and approved detailed calculations. All rails, clamps, brackets, bolts and accessories included. | 1 | lot | TR-MNT-01–08 | 25-year rooftop structure, C5-M, SS fasteners
9 | PV Mounting for baywalk | Canopy PV mounting structure | Standalone canopy PV structure with minimum 4.5 m clearance, marine-grade hot-dip galvanized steel or equivalent with minimum 85 µm coating and 20-year corrosion protection with an additional paint coating incorporating a Papuan painting pattern, watertight full-shade design with durable module to module sealing, structure designed for SNI and site wind/seismic loads minimum 40 m/s ultimate, and PV mounting system compatible with and approved by PV module OEM. | 1 | lot | TR-MNT-09 | 25-year canopy structure, C5-M, SS fasteners
D | Electrical BOS Component
10 | BOS Electrical | PV DC Cable | PV DC system rated maximum 1,500 Vdc, complete with 1.5 kVdc-rated components, tinned copper flexible PV cables minimum 1x6 mm², certified DC connectors, and design verified for string voltage, current, inverter compatibility, voltage drop, derating, environmental conditions, and outdoor/coastal durability. | 1 | lot | TR-DC-01 - 02 | 1.5 kVdc PV1-F tinned copper, ≥6 mm²
11 | BOS Electrical | Battery DC Cable | Flexible copper DC battery cable for the battery system, with XLPO/XLPE insulation and LSZH sheath, suitable for nominal battery voltage operation and the required battery current. It shall be complete with cable lugs, insulation, polarity identification, and all accessories compatible with the battery and inverter terminals. Cable size shall be selected based on continuous current, voltage drop, installation method, short-circuit withstand, and the requirements of the battery and inverter OEMs. | 1 | lot | TR-BESS-11 | 0.6/1 kV, flexible cable, XLPE, LSZH
12 | BOS Electrical | AC Cable | Stranded copper LV AC power cable, minimum 0.6/1 kV, XLPE insulated, with LSZH sheath for indoor use and UV/weather/moisture-resistant sheath for outdoor use, suitable for tropical/coastal environment, minimum conductor size 2.5 mm² or as required by calculation, with sizing based on ampacity, voltage drop, and short-circuit withstand, and complete with corrosion-resistant glands, lugs, identification, and accessories. | 1 | lot | TR-AC-8 | 0.6/1 kV, XLPE insulated, with LSZH sheath
13 | BOS Electrical | Communication cable | Communication cables for Ethernet, RS485, and CAN bus applications, using shielded copper twisted pair construction with UV/weather-resistant sheath for outdoor use or LSZH for indoor use, suitable for industrial installation, with required impedance/performance for the protocol, flame-retardant where applicable, and complete with manufacturer test certificate. | 1 | lot | TR-COM-01 - 03 | Communication cables for Ethernet, RS485, and CAN bus applications
14 | BOS Electrical | Cable tray | Indoor and outdoor cable tray, ladder, cover, bracket, and support system using hot-dip galvanized steel minimum 85 µm with marine coating, tray covers and sealant for animal protection, SS316 outdoor fasteners, and neat elevated installation for protected cable routing between PV areas and powerhouse without obstructing access or maintenance. | 1 | lot | TR-BOS-01, 03 | Hot-dip galvanized steel minimum 85 µm with marine coating
15 | BOS Electrical | Cable conduit | Complete conduit and cable containment system using heavy-duty UV-resistant or corrosion-resistant materials suitable for indoor/outdoor/coastal conditions, with liquid-tight fittings where required, sealant against animal intrusion, proper fill ratio, and neat cable installation with spacing, support, and derating consideration. Conduits for outdoor exposed installation shall be minimum HDPE or hot dip galvanised rigid steel conduit as suited to the location. | 1 | lot | TR-BOS-02 - 03 | HDPE or hot dip galvanised rigid steel conduit as suited to the location.
16 | BOS Electrical | Electrical BOS, and cable accessories | Cable accessories including indoor cable ties, MC4, outdoor SS cable ties with epoxy coating, tinned copper compression lugs, ferrules, glands, heat-shrink, stainless steel cable tag with embosed markers, and sealing accessories, suitable for indoor, outdoor, and coastal installation. | 1 | lot | TR-BOS-08 | MC4, SS ties epoxy coated, SS cable and equipment tag
17 | BOS Electrical | Earthing and lightning system | Complete integrated earthing and lightning protection system for PV, BESS, panels, and metallic parts, with coordinated AC/DC/communication SPDs, target earth resistance maximum 5 Ω, bonding continuity maximum 0.3 Ω, complete accessories, and full testing and commissioning records. | 1 | set | TR-EAR-01 -06 | Copper rod, clamps, franklin rod
18 | PV Inverter AC Combiner panel | PV Inverter AC Combiner panel | AC combiner box for PV inverter outputs, suitable for 230/400 V AC, 3-phase, 4-wire, 50 Hz, complete with busbar, MCCBs, isolation, SPD Type I+II, neutral and earth bars, bypass switch, and required monitoring/control terminals, with minimum IP54 corrosion-resistant enclosure for tropical conditions, protective barriers, internal cable management, routine test report, and compliance with IEC. | 1 | set | TR-AC-05 | AC combiner box for PV inverter outputs, suitable for 230/400 V AC, 3-phase, IP54
19 | Battery DC Combiner panel | Battery DC Combiner panel | Battery combiner panel complete with DC MCCBs, busbar, isolation, positive/negative/earth bars, and externally accessible load break switch or DC isolator, minimum IP54 corrosion-resistant enclosure for nearshore conditions, with insulated busbars, internal cable management, protective barriers, factory finish, routine test reports. | 1 | set | TR-BESS-05 - 07 | Battery combiner panel complete with DC MCCBs, IP54
20 | Main distribution panel | Main distribution panel | Main AC distribution panel for 3-phase 400/230 V, 50 Hz system, complete with breakers, RCBOs, busbars, terminals, change-over/bypass/isolation devices, Type I+II surge protection, energy meters, and monitoring feedback, protective barriers, suitable for connection of PLN, PV, and BESS systems, with coordinated protection and selectivity, minimum 20% spare capacity for load feeder, minimum IP54 corrosion-resistant enclosure where applicable, and complete shop drawings, test reports, and control/interlock details. | 1 | set | TR-AC-01 - 04 | Main AC distribution panel for 3-phase 400/230 V, 50 Hz system, complete with breakers, RCBOs, busbars, terminals, change-over/bypass/isolation devices, Type I+II surge protection, energy meters,
21 | Communciation interface panel and CCTV | Communciation interface panel and CCTV | Communication and SCADA panel complete with RTU/data logger, switches, power supplies, protective devices, grounding bars, and minimum 8-hour UPS backup, in minimum IP54 corrosion-resistant enclosure suitable for near-shore indoor installation, with proper cable segregation and shop drawings, together with CCTV system covering the power house interior, entrance, and surrounding area for security and safety monitoring. | 1 | set | TR-MON-11 - 12 | Communication and SCADA panel, UPS, CCTV
E | Monitoring and control system
22 | Monitoring | Control and monitoring system | Complete local and online monitoring system for PV, BESS, inverter, meters, breakers, alarms, events, trends, KPIs, and environmental data, web/local interface, minimum 1–5 minute logging, event records, user access for Contracting Authority, minimum 10-year platform/license validity, local monitoring PC with 27-inch display and 40-inch display screen, and full access to all operational data without vendor lock-in. Internet connectivity equipment and data during EPC warranty period shall be provided | 1 | set | TR-MON-01 - 10 | Complete local and online monitoring system or mini SCADA system. Including PC, display, RTU, switches, modem, etc.
23 | Monitoring | Weather sensor | Weather station complete with pyranometer, ambient temperature sensor, and relative humidity sensor, suitable for outdoor PV monitoring, with communication output, required accuracy, proper mounting and placement, and all accessories for complete installation and commissioning. | 1 | set | TR-MON-06 | Weather station complete with pyranometer, ambient temperature sensor, and relative humidity sensor
24 | Monitoring | Revenue meter | Three-phase, four-wire CT-operated energy meter, minimum Class 0.5S, suitable for 400 V, 50 Hz system, with bidirectional measurement, load profile, event logging, Modbus communication, and complete with CTs, terminals, enclosure, sealing, testing, calibration, and commissioning. | 1 | set | TR-MON-07 | Three-phase, four-wire CT-operated energy meter, minimum Class 0.5S
25 | Monitoring | Energy meter | AC metering system for PV generation, battery charge/discharge, each facility loads, PLN incoming, and Inverter AC combiner box outputs, with minimum Class 0.5 accuracy, compatible with monitoring and zero-export control system, and complete with defined measurement points, CTs, communication wiring, and data mapping. | 1 | set | TR-MON-08 | Single/three phase, four-wire CT-operated energy meter, minimum Class 0.5 accuracy, compatible with monitoring and zero-export control system
F | Civil, structural, and mechanical works
26 | Civil works | Power house | Prefabricated modular power house suitable for severe coastal/near-shore outdoor installation, with insulated weatherproof construction, minimum IP54 protection, corrosion-resistant materials and SS316 external hardware, sufficient space and minimum 1.5 m maintenance clearance, floor and structure designed for actual equipment loads, and HVAC sized to maintain required internal environmental conditions. | 1 | set | TR-CW - 03, 07 | Prefabricated modular power house, fire alarm and fighting system, HVAC
27 | Civil works | Building roof enhancement | Structural strengthening works for PV mounting system and/or roof to support PV canopy installation, including additional steel, bracing, plates, anchors, fasteners, corrosion protection, installation, and structural compliance documentation. | 1 | lot | TR-CW-02 | Structural strengthening works for PV mounting system and/or roof to support PV canopy installation
28 | Civil works | Civil works | Reinforced concrete foundation for PV canopy and power house, including general arrangement drawings, foundation design calculations, excavation, backfilling, reinstatement, drainage restoration, and all related civil works, based on structural and geotechnical design requirements and restoring the area to its original functional condition. | 1 | lot | TR-CW-01, TR-CW-04 - 06 | concrete foundation for PV canopy and power house
29 | Cleaning system | Water cleaning systsm | PV cleaning system complete with water tank, booster pump, piping, hose points, hoses, and manual cleaning accessories, providing adequate flow and pressure for safe module cleaning, with UV-resistant and corrosion-resistant materials suitable for outdoor tropical conditions. | 1 | set | TR-BOS-07 | PV cleaning system complete with water tank, booster pump, piping, hose points, hoses, and manual cleaning accessories
G | Spare parts
37 | O&M | Spare part | Spare parts include commissioning spares and minimum 5-year operational spares for major PV, BESS, electrical, control, and communication equipment, with quantities, storage conditions, and replacement responsibility, including minimum 0.5% or 6 spare PV modules, whichever is higher, and minimum 1–3% spare consumables. | 1 | lot | TR-DOC-05
Total Componen (A- G)
H | EPC service cost
34 | Construction | Engineering, Installation, Construction, Commissioning & Project Management (PMT) | Include project management, site visit, engineering, installation, construction, commisioning, training, heavy duty equipment, HSE, warehouse, field assessment, O&M Training, QA/QC, construction insurance (CAR), functional testing, protection checks, permits (PLN and SLO), commissioning, and performance test. | 1 | lot
35 | Procurement & Logistics | Logistics | Logistics to KNMP Biak,Papua | 1 | lot
36 | O&M | Preventive maintenance | Provision of scheduled preventive maintenance service for PV and DC-coupled BESS system including visual inspection, cleaning of inverter ventilation, torque checking of electrical terminations, inspection of DC/AC cables and conduits, grounding continuity check, inverter functional verification, battery system health review (SoH, alarms, logs), firmware status check, communication verification (Modbus/CAN), thermographic inspection of electrical panels, and submission of maintenance report with findings and recommendations. Includes manpower, tools, testing instruments, minor consumables, and travel for 2x visit/year. | 1 | lot
I, the undersigned, certify that I am duly authorized by [insert full name of bidder] to sign this quotation and bind [insert full name of bidder] should GIZ accept this quotation:
Name: [complete]
Title: [complete]
Date: [complete]
Signature and company stamp:

## Terms and Conditions
| TERMS AND CONDITIONS | Please tick "Yes" or "No" |  | Deviations
|  | Yes | No
1 | Product shall be delivered by the contractor after the PO release. Delivery date estimation:
2 | The contractor shall deliver the goods within 30 days after signing the Purchase order (date) in the delivery address as mentioned above Delivery Address: On Behalf of Project Cooperation with GIZ Kampung Nelayan Modern (Kalamo) Biak Samber, Yendidori, Biak Numfor Regency, Papua
3 | Validity of Quotation is 60 calendar days
4 | Payment terms: Advance payment (25%) from total cost upon contract effectiveness and readiness for mobilization Interim Payment 1 (40%) from total cost upon approval of the detailed engineering and procurement package, and delivery of all major equipment and bulk materials to site. Interim Payment 3 (30%) from total cost upon completion of installation and readiness for commissioning; and successful cold & hot commissioning, training, and handover for operation Final Payment (5%) from total cost upon expiry of defects liability period and closure of outstanding defects.
5 | All prices/rates quoted must be exclusive of all taxes, since the GIZ, including its subsidiary organs, is exempt from taxes according to PMK No. 215/PMK 03/2008 and KMK No. 17/KMK 010/Year 2021. GIZ shall process the VAT with tax restitution to BADORA. Supplier is obliged to release the Tax Invoice with code 04 (tax restitution). Please provide the PKP and PTKP Letter.
6 | Supplier Self-Declaration to determine the origin or source of the goods offered shall be signed and attached with the tender document (obligatory) – as annex 3
7 | Declaration of Prevention of Terrorism shall be signed and attached with the tender document – as annex 4
8 | Items original with official warranty
9 | The contractor shall demonstrate verifiable experience in the design, supply, installation, and commissioning of off grid, on grid system and hybrid solar PV systems, preferably with battery storage (BESS) and inverter integration with SMA systems to ensure overall compatibility as per required design.
10 | The contractor has at least three (3) successfully completed projects of similar size (≥50 kWp solar PV, battery system, hybrid inverters) within the last five (5) years with attach the documentation/ photos.
11 | The contractor ensures the permit and regulation compliance as the solar PV system will be connected to the PLN electricity grid, including NIDI, PLN Application, IUPTLS, SLO (Sertifikat Layak Operasional)
12 | The Contractor shall demonstrate availability of spare parts and qualified service personnel within Java, Indonesia for the full warranty period. Include provide the list of recommended critical spare parts, Location of spare parts storage, Lead time for replacement components.
13 | The contractor must provide SBUJPTL (Sertifikat Badan Usaha Jasa Penunjang Tenaga Listrik), issued by Lembaga Sertifikasi Badan Usaha (LSBU) that has been accredited or appointed by the Minister of Energy and Mineral Resources.
14 | Installation personnel must provide SKKTK (Sertifikat Kompetensi Tenaga Teknik Ketenagalistrikan) issued by The Ministry of Energy and Mineral Resources, where the supervisor has a minimum of Level 5 SKKTK on PV system installation.
15 | The contractor shall have an established local office or partner in Java, Indonesia to ensure responsive after-sales service, maintenance, and warranty support. During the warranty period, The Contractor shall provide remote diagnostic support throughout the warranty period. The Contractor shall provide remote corrective maintenance with a maximum response time of 24 hours from fault notification. On site intervention shall occur within a maximum of 72 hours (subject to travel logistics to Biak). Critical system faults affecting energy supply shall be prioritized.
16 | The contractor must have Health, Safety, and Environmental Compliance (e.g.: Use of appropriate personal protective equipment (PPE) during installation.)
17 | The contractor must comply with national electrical and construction safety standards, manufacturer installation manuals, project-specific technical requirements and commissioning (i.e.: Implementation of best practices to prevent damage to the roof and solar equipment.)
18 | The contractor review all drawings and specifications, notify any discrepancies and submit a detailed drawing to GIZ maximum 3 weeks after signing the contract.
19 | The contractor will conduct site visit to Kalamo/KNMP Biak prior to start of installation to verify conditions, access, and interfaces.
20 | The contractor will coordinate arrangements and timeline with GIZ and Dinas Kelautan Perikanan (representative from Kalamo/KNMP Biak) regarding supply, civil and structural works, installation, and post installation.
21 | The Contractor should be responsible for the packing/pre-assembly.
22 | The contractor provides a warehouse to store equipment prior to delivery on site
23 | The contractor will be responsible for goods transport to the site and installation of the system
24 | The contractor will install the PV modules and mounting structure in the roof, ensuring all modules are installed with appropriate spacing, grounding, and mechanical fixation as per technical guidelines
25 | After installation, the contractor shall submit the Fit for Operational certificate (Sertifikat Layak Operasional) issued by LIT (Lembaga Inspeksi Teknik).
26 | A final test will be carried out to demonstrate that the Systems can be operated according to the technical specifications under all available operating conditions
27 | The contractor shall submit a quality checklist, along with the completeness of drawings, operation and maintenance manuals, witnessed and approved by GIZ
28 | The contractor shall complete the supply and transport equipment to site, installation of equipment, including the materials provided by GIZ, and the test and commission of the installation within Q3 2026
29 | The contractor will provide 2 Maintenance services at 6th month and 12th month after commissioning
30 | The contractor must provide a minimum of two (2) years warranty on the entire system and components (only the owns that have been delivered) against manufacturing defects and all installation work performed by the contractor. During this period, contractor shall remain responsible for coordination and facilitation of all warranty claims with manufacturers.
31 | After the expiration of the system warranty, the contractor will be responsible only for component replacement and transportation to the GIZ office in Indonesia, but not for labor costs, during the minimum warranty periods of the key components (PV Inverter, BESS).
I, the undersigned, certify that I am duly authorized by [insert full name of bidder] to sign this quotation and bind [insert full name of bidder] should GIZ accept this quotation:
Name: [complete]
Title: [complete]
Date: [complete]
Signature and company stamp: