## Specifications
Position | Item | Description | Remarks The comparative specification should indicate any deviation from the technical parameters or functional description of the tender documents. If there is no deviation from the technical specification in columns A-C, please indicate "Yes". Otherwise, describe your special features in this column. | Quantity / Capacity | Unit
1 | General Requirements
1.1 | PV Plant | see next spread sheet |  |  | kWp
1.2 | Site description | see next spread sheet
1.3 | Power grid | The PV systems are to be hybrid system - to balance the benefits of solar generation with grid electricity. The specifications of the grid operators are to be completely fulfilled technically especially the need to limit export to the grid for buildings without net-meters. The PV systems shall meet applicable Ghana Building Code and National Electricity Distribution Code requirements as well as other prudent best practices.
1.4 | Preliminary design principles | The contractor shall propose a solar plant with battery design and integration drawings, undertake the installation of the system, and conduct maintenance of the system for one year. The drawings and schematic layouts must indicate one-line electrical diagram showing inverters, combiner box, batteries, etc. The contractor shall provide references of database and software used for the design. All components offered must comply with below technical requirements and fully functional and compatible with each other. All components and parts that are not explicitly mentioned in this document, but are necessary to ensure a faultless layout, installation and professional operation must be offered by the bidder (except for parts that are explicitly excluded from the tender).
2 | Photovolatic Modules
2.1 | Photovoltic Modules | The module shall meet the following technical requirements, minimum standards and specifications: - the minimum technical specifications of the proposed nominal capacities [1.1] - 60 or 72 cell PV modules with crystalline technology - Output per module min. 280 Wp (60 cells) / 330 Wp (72 cells), tolerance 0 - 5%. - Certification for wind load up to minimum 2400 Pa - Solar cells shall be embedded in an EVA (ethylene vinyl acetate) layer, anti-reflective coating, front cover made of specially tempered, highly transparent glass. Framed with aluminium profile (anodised). - Maximum NOCT 45±2°C. The PV modules shall be capable of operating under extreme temperature (up to +50°C) and humidity (up to 95%) conditions. |  |  | No.
2.2 | Certifications and standards | The module complies with the following standards and certifications: - IEC 61 215 : Terrestrial photovoltaic (PV) modules - Type qualification and type approval. - IEC 61 730 : Photovoltaic (PV) modules - safety qualification The tests are carried out by recognised testing laboratories according to ISO/IEC 17025. The manufacturer of the solar modules can prove by a suitable certificate that a permanent quality control and assurance of the production processes takes place in his factory. It must be proven that the standards according to IEC 61215 and IEC 61730 are also adhered to in ongoing production. The certificate itself is issued by an accredited testing institute. The normative requirements IEC 60891 ; IEC 60904 ; IEC 61345 ; IEC 61701; IEC 61721; EN 50380 are fulfilled. CE Declaration of Conformity by the manufacturer is available. A confirmation by a conformity assessment body according to ISO/IEC 17021 is available. CE marking of the solar modules is available. The solar modules are marked accordingly. Weatherproof junction box on the back of the module. The junction box must comply with at least IP 65 and the DIN VDE 0126-5 standard. The cabling between the modules with connectors complies with the EN 50521 standard.
2.3 | Warranty | Linear performance guarantee for 25 years with maximum degradation coefficient of -0.5%/year Product guarantee for at least 10 years If the rated power of the modules is undershot within the guaranteed warranty period, the modules will be replaced free of charge at the installation site. |  |  | yrs
2.4 | Please specify: | Brand name, model, type
|  | Area of the cells (LxW) in mm |  |  | mm
|  | Dimensions of the module (LxWxD) in mm |  |  | mm
|  | Weight of module in kg |  |  | kg
|  | Maximum power (Pmax) W |  |  | W
|  | Maximum voltage ( Vmax) V |  |  | V
|  | Maximum current ( Ipmax) A |  |  | A
|  | Maximum reverse current IR [A] |  |  | A
|  | Short-circuit current (Isc) A |  |  | A
|  | Open circuit voltage ( Voc) V |  |  | V
|  | Temperature coefficient for current A/°C |  |  | A/°C
|  | Temperature coefficient for voltage V/°C |  |  | V/°C
|  | Temperature coefficient for power %/°C |  |  | %/°C
|  | Nominal cell operating temperature ( NOCT) |  |  | NOCT
|  | Maximum system voltage ( Vsmax ) |  |  | Vsmax
|  | Operating temperature ( Min- Max ) °C |  |  | °C
|  | Ambient temperature ( Min - Max ) °C |  |  | °C
Current-voltage characteristics at 25°C and other temperatures and irradiation
3 | Panel Structure
3.1 | Requirement | Compliant with Ghana Fire Service code and ordinance requirements for roof access; and all applicable Ghana Building Code and local assembly codes and standards. Structure design shall address access for maintenance and replacement of the equipment. All structural components shall be non-corrosive (galvanized steel, stainless steel or aluminium).
3.2 | Warranty | min. 10 years |  |  | yrs
3.3 | Please specify: | Brand name, model, type
Data sheet
Detailed description of the anti-theft screws and nuts
Technical description of the substructure (angle of tilt, etc)
Anti-theft bolts and nuts to match the modules
Description of the lightning protection and earthing
4 | Inverter
4.1 | Hybrid Inverter | The hybrid inverter shall meet the following requirements, minimum standards and specifications: - meets the minimum technical requirements of the Electricity Company of Ghana as well as the technical specification of the current National Electricity Distribution Code. - Compatible with supplied storage batteries - Forced air or natural convection cooling method - Wall-mounted or floor-standing - In-built charge controller (MPPT) - Enables supply of consumers with 230 V AC - Simultaneously allows connection to a battery bank or power grid - Capable of integrating a battery storage and caharging a battery bank - Continuous power min. 20kW - System voltage 48 V - Output voltage 230 V AC +/- 5% - Output frequency 50/60 Hz - Pure sine wave voltage - Integrated MPP tracker, multi-stage charging technology - Adjustable end-of-charge voltages - Adjusted to the interconnecting solar modules from positions - Input voltage 90 - 280 V AC - Input frequency 40 - 65 Hz; Automatic recognition 50/60 Hz - Max.current on transfer system 120 A - Efficiency >90% - Harmonic distortiion <3% |  |  | No.
4.2 | Certifications and standards | It must comply with the following standards: EN-IEC 60335-1, EN-IEC 60335-2-29, EN-IEC 62109-1, EN 55014-1, EN 55014-2, EN-IEC 61000-3-2, IEC 61000-6-1, IEC 61000-6-2, IEC 61000-6-3. Manufactured according to ISO 9001 and ISO 14001. CE compliant
4.3 | Warranty | min. 5 years |  |  | yrs
4.4 | Please specify: | Brand name, model, type
Waveform
|  | Dimension (LxWxD) in mm |  |  | mm
|  | Weight of module in kg |  |  | kg
|  | Maximum power (W) |  |  | W
|  | Nominal Ccontinuous power (W) |  |  | W
|  | Input Current (A) |  |  | A
|  | Nominal input voltage (VDC) |  |  | VDC
|  | Input voltage range (VDC) |  |  | VDC
|  | Nominal output voltage (VAC) |  |  | VAC
|  | Number of MPPT Trackers |  |  | No.
|  | AC voltage range (%) |  |  | %
|  | Voltage regulation (%) |  |  | %
|  | AC power frequency (Hz) |  |  | Hz
|  | Maximum ambient temperature (°C) |  |  | °C
|  | Max Charging Current (A) |  |  | A
Communication/interfaces: RS485, USB, Ethernet
|  | Efficiency (%) |  |  | %
Transformerless inverter protection class (IP)
MPPT Operating Voltage Range
Integrated data logger
|  | Permissible humidity (%) |  |  | %
IP Rating (indoor & outdoor)
Data sheet
5 | Battery
5.1 | Lithium-ion-battery | The lithium-oin battery shall meet the following requirements, minimum standards and specifications: - 3,000 cycles @50% DoD, 20°C / 1,500 cycles @80% DoD, 20°C [for smaller only 2,500 @50 DoD 20°C] - Proof of conformity and performance: IEC 60896-21/22 and IEC 61427-2 is required. - Service life according to EUROBAT min. 12 years at 20°C - Standards and regulations for installation: DIN EN 50272-2 (safety regulations for battery rooms) - The battery must be supplied with its rack certified by the manufacturer. - Proof of quality assurance system according to ISO 9001 / ISO 14001 - ISO 45001;IEC 62619, UL 1973 occupational health and safety or equivalent certification - Integration with hybrid inverters and monitoring apps - Fully insulated, corrosion-free lead terminal - All pole penetrations must ensure complete electrolyte and gas tightness even when positive plate is growing - Fully insulated copper connectors and screw heads - Interconnection lead poles with torque 20 - 22 Nm - Environmentally friendly, min. 98 % recyclable - Energy efficiency > 80% - Ampere-hour efficiency > 90% - Self-discharge less than 2-3%/month at 20°C - No memory effect - Sufficiently large containers for electrolyte circulation - Each battery is labelled with at least the following data: Manufacturer, type, model number, nominal voltage in V, nominal capacity in Ah, month and year of commissioning. - Each cell must have a factory serial number Protection functions: - Short-circuit proof - Cell balancing - Overload protection - Deep discharge - Overcharging - Overtemperature protection |  |  | No.
5.2 | Please specify: | Brand name, model, type
|  | Nominal Voltage |  |  | V
|  | Nominal Capacity |  |  | Ah
|  | Energy Capacity |  |  | kWh
|  | Weight of module |  |  | kg
|  | Voltage Range per cell |  |  | V
|  | Depth of Discharge (DoD) |  |  | %
|  | Cycle Life (@50% or 80% DoD) |  |  | A
IP Rating (indoor & outdoor)
Data sheet
5.3 | Warranty | min. 5 years |  |  | yrs
7 | Cable, Combiner Box, Connectors and Distribution Panel
7.1 | Requirement | The wiring, combining box, connectors and distribution panel(s) shall meet the following requirements, minimum standards and specifications: - All wiring between combiner box, surge protection, distribution panel and the point of interconnection shall meet applicable codes. - Wiring and connections shall fulfil these standards and conditions; TUV PfG 1169/08.2007, EN 50396, IEC/EN 60332-1-2, HD 605/A1, EN 50267-2-1, EN 60684-2, IEC /EN 60811-2-1, EN 50267-2-2, HD 605/A1, EN 50521 and Direct Current wiring loss-es max. 1.5%. - Distribution panel, combiner box and lighting protection shall fulfil these standards and conditions (where applicable); IEC 60364, KS 04-192: 1988, KS 04 -194: 1990, KS 04 -187/188, KS 04 -290: 1987, IEC 62305, KS 04-179: 1983; UV and water-resistant material, MCB / MCCB outdoor cabinets and enclosures, SPDs class II - IEC 61643-11 and operating temperature up to 80°C, non-metallic fiberglass enclosures with clear polycarbonate covers
7.2 | Cables | 1x [4, 6 or 10] mm² copper cable with double insulation for up to 1000V, type C2 (high flame resistance), AN3 (high UV resistance) Maximum permissible conductor temperature at least 90°C in continuous use. The standard EN 50618 is fulfilled. All AC power cables shall comply with IEC 60502-1 and IEC 60228, featuring copper conductors, XLPE insulation, and low-smoke halogen-free (LSZH) sheathing. Cables installed outdoors must be UV-resistant and weather-proof. All cables shall be rated for continuous operation at a maximum conductor temperature of 90°C. |  |  | lot
7.3 | Empty conduits | PE cable conduits for burial, double wall (corrugated outside, smooth inside according to standard NF EN 50086-2-4) |  |  | lot
7.4 | Cable ties | UV-resistant cable ties in all necessary sizes and quantities. |  |  | lot
7.5 | Accessories | All accessories for proper fastening of the cables under the modules for the entire installation. |  |  | lot
7.6 | AC or DC combiner box |  |  |  | No
7.7 | Switch cabinet / Automatic Change Over |  |  |  | No
7.8 | Earthing system |  |  |  | lot
8 | Documentation
| The following documentation, manuals and software in English, must be supplied in electronic form for all components of the system after the order has been placed: | For documentation, IEC 62446-1:2016 standard shall be fulfilled by contractor. Assembly instructions for the entire system. Overview for an installer on site, showing which components are connected to each other and how. This overview also refers to the corresponding installation instructions and assembly instructions for the individual components.
Overview of proposed solar PV plant and performance characteristics
Circuit documentations
Description of the components
Wiring diagrams, layouts, scheme of switches and combiner boxes
Assembly instructions, installation instructions
Commissioning instructions
Operating & maintenance instructions / manual
Manual, Data sheets and Maintenance instructions
Error analysis and troubleshooting suggestions in the event of a malfunction
ALL Warrantees
9 | Delivery
9.1 | Customs clearance | To be managed by the bidder The bidder must be able to offer customs clearance and import of all required items in Ghana. The bidder shall undertake the complete process of customs clearance and importation. The handling costs for this are to be listed in the bid. Customs duties and import tax shall be addressed by bidder. The bidder must have all required licenses and accreditation to import solar plant materials in Ghana.
9.2 | Domestic transport | To be managed by the bidder. All items must be delivered to each site.
see next spread sheet
9.3 | Deadline | see next spread sheet
10 | Installation
| Please enclose with the offer: | Installation roadmap for each site for approval by the GIZ technical team
Prove that only qualified / experienced experts shall undertake the installation and commissioning of system (e,g, Energy Commission certified electrician license, CV, etc)
Installation and commissioning of all components and the complete PV-System. The supplier shall be responsible for carrying out of all related electrical works and supplying of all necessary electrical equipment for the proper operation of the supplied technological equipment. Installation and commissioning at the site must be conducted according to Ghana electrical quality and safety norms and standards. Certified solar technicians should perfom the solar installation and commissioning. Complete inspection, testing and commissioning of the PV-System incl. function tests and trial operation.
Necessary planning and preparation work before installation have to be considered and taken care of. The project, including supports and power conductors, shall not interfere with roof drains, water drainage, expansion joints, air intakes, existing electrical and mechanical equipment, existing antennas, and planned areas for future installation of equipment shown on existing drawings.
Documentation: All work steps will be documented in detail throughout the installation phase. The documentation will include the final (actual) wiring diagram of all components and the PV-System. The contractor shall deliver a completion report containing “as-built drawings" and all other project documents based upon actual site installation. The contractor shall submit two (2) hard copies and two (2) pen drives containing the “as-built” drawings/designs and specifications as CAD and PDF files.
Indication of what kind of service can be provided (spare parts procurement, spare parts exchange, fault analysis with repair etc.)
11 | Maintenance
11.1 | 1 year after commisssioning | 2 regular maintenance per year
11.2 | Maintenance plan | 1 year maintenance roadmap for each site - to be approval by the GIZ technical team

## Site Description
0.1 | 0.2 | 0.3 | 1.0 | 1.1 | 1.2 | Remarks
No | System Description | Region | Site name | PV Plant Description | Site Description
1 | 7kWp (A) | Greater Accra Region | PRESEC - Legon | Nominal solar plant capacity at least 7 kWp [Nominal battery capacity at least 7 kWh] - Rooftop mounted solar PV system - With back-up storage batteries - Hybrid solar PV system procurement, installation, and one (1) year system maintenance | The plant is to be erected in Accra, Greater Accra Region GPS Location: - 5°39'48.0"N 0°10'28.0"W (https://maps.app.goo.gl/2MmnhAiQVGw5DPiu7) | The final building and roof for the installations will be confirmed after contract award in consultation with the Sponsor, Beneficiary Facility, and the selected Contractor. Bidders shall base their financial proposals on the baseline system specifications and standard cable routing assumptions provided in this Tender Document. Any additional accessories, extended cable runs, or other site-specific requirements identified shall be subject to confirmation and agreement by all parties and managed through the applicable contract variation procedure. Delivery Deadline: 1 Month after signing of contract
2 | 4kWp (A) | Western Region | Ahantaman Girls SHS | Nominal solar plant capacity at least 4 kWp [Nominal battery capacity at least 4 kWh] - Rooftop mounted solar PV system - With back-up storage batteries - Hybrid solar PV system procurement, installation, and one (1) year system maintenance | The plant is to be erected in Sekondi, Western Region GPS Location: 4°57'30.8"N 1°43'45.6"W (https://maps.app.goo.gl/uVP5RN3aw4JNYWy67)
3 | 7kWp (B) | Greater Accra Region | Energy Commission | Nominal solar plant capacity at least 7 kWp [Nominal battery capacity at least 7 kWh] - Rooftop mounted solar PV system - With back-up storage batteries - Hybrid solar PV system procurement | To be delivered without installation
4 | 4kWp (B) | Greater Accra Region | Energy Commission | Nominal solar plant capacity at least 4 kWp [Nominal battery capacity at least 4 kWh] - Rooftop mounted solar PV system - With back-up storage batteries - Hybrid solar PV system procurement | To be delivered without installation