## BOQ
BILL OF QUANTITIES (BOQ) – SOLAR PV SYSTEM (20 kW 3-PHASE HYBRID)
Date: 5 May 2026
Company Name
Item No. | Description | Specification | Unit | Quantity | Unit Rate (ZMW) | Total (ZMW)
1. MAJOR EQUIPMENT
1.1 | 3-Phase Hybrid Inverter | 20 kW, 400V, with MPPT & protections | Ea | 1 |  | 0
1.2 | Solar PV Modules | 550W mono-crystalline | Ea | 36 |  | 0
1.3 | Lithium Battery | 5 kWh, 51.2V, 100Ah, LiFePO4 | Ea | 8 |  | 0
2. PV MOUNTING STRUCTURE
2.1 | Mounting Structure for the panels | Aluminium/galvanized steel, complete set | Lot | 1 |  | 0
3. DC SIDE (PV)
3.1 | DC Combiner Box | IP65 complete with busbars and terminals | Ea | 1 |  | 0
3.2 | PV DC Cable (Red) | 6mm², single-core, 1500V DC | m | 45 |  | 0
3.3 | PV DC Cable (Black) | 6mm², single-core, 1500V DC | m | 45 |  | 0
3.4 | DC Isolator | 1000V DC, 32–40A | Ea | 3 |  | 0
3.5 | DC SPD | Type II, 1000V DC | Ea | 3 |  | 0
3.6 | Main DC Isolator | Type II, 1000V DC | Ea | 1 |  | 0
3.7 | DC Surge Protection Device (SPD) | Type II, 1000V DC | Ea | 1 |  | 0
4. BATTERY SIDE
4.1 | Battery Cable | 2C x 70mm² copper DC cable | m | 30 |  | 0
4.2 | Battery Interconnection Cable | 35mm² copper | m | 10 |  | 0
4.3 | Battery DC Breaker | 125A, 1000V DC | Ea | 1 |  | 0
5. AC SIDE
5.1 | Inverter to MDB Cable | 4C x 16mm² copper cable | m | 5 |  | 0
5.2 | Grid/Generator Cable | 4C x 50mm² copper cable | m | 10 |  | 0
5.3 | AC Distribution Board | IP65 enclosure complete with DIN rail, busbars, gland plate, terminals | Ea | 1 |  | 0
5.4 | AC MCCB | 4P 63A | Ea | 1 |  | 0
5.5 | AC Isolator | 4P, 63A | Ea | 1 |  | 0
5.6 | AC SPD | Type II, 400V AC | Ea | 1 |  | 0
6. MDB & PROTECTION
6.1 | Main Distribution Board | 250A, 4P busbar, IP54 | Ea | 1 |  | 0
6.2 | Inverter MCCB | 4P, 63A, 36kA | Ea | 1 |  | 0
6.3 | Grid MCCB | 4P, 100A, 36kA | Ea | 1 |  | 0
6.4 | Generator MCCB | 4P, 100A, 36kA | Ea | 1 |  | 0
7. EARTHING & ACCESSORIES
7.1 | Earth Rod | Copper bonded, complete set | Ea | 2 |  | 0
7.2 | Earthing Cable | 16mm² copper | m | 30 |  | 0
7.3 | Cable Trunking & Conduits | PVC/HDPE, complete | Lot | 1 |  | 0
7.4 | Bentolite (for earthing) | 25 Kg bags | Kg | 1 |  | 0
7.5 | Other accessories (Cable Lugs, Glands, MC4 Connectors, Fisher Plugs) | Complete set | Lot | 1 |  | 0
8. INSTALLATION & SERVICES
8.1 | Transport | Delivery to Mansa | Lot | 1 |  | 0
8.2 | Installation, Commissioning and Training | Complete | Lot | 1 |  | 0
8.3 | Provision for Flexible Remuneration | Provisional | Lot | 1 |  | 0
Total: | [5 empty] | 0